## Sign-Off Sheet
Hotel Europejski
,
Switch Function Table Approval
|  | Switch Table: | Design:
|  | Switch Table Date: | Design Date: | 2016-03-09 10:03
Approved:
Date:
APPROVAL OF DESIGN IS REQUIRED PRIOR TO ANY PROGRAMMING OF INNCOM DEVICES. NO REPLY REGARDING APPROVAL DOES NOT CONSTITUTE ACCEPTANCE OR APPROVAL OF DESIGN.
Revision History
Date | Revision | Comments

## MOCKUP
INNCOM Switch Function Table
| Designer: | Maciej Jakubiak | [5 empty] | Design: |  |  |  | 2017-07-19 | [5 empty] | 2017-07-19 |  |  | Design Date:
| Hotel Europejski |  |  |  |  | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes |  | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes |  | Controlled Zones/ Drapes | [5 empty] | Controlled Zones/ Drapes | Controlled Zones/ Drapes
| TypK_Flr2 |  |  |  |  | 6.1 Toilet Accent | 6.2 Toilet Main | 7.1 Cabinet Bed | 7.2 Bed Screen | 8.1 Bedroom Main | 8.2 Bedroom Artwork | 9.1 Cabinet 1 Saloon | SPARE | 10.1 LED Toilet | 10.2 Main LED Bedroom | 11.1 Library saloon | 11.2 Main LED Saloon | 21.1 Cabinet 1 Bedroom | 20.2 Lamps Bathroom | 22.1 Saloon Artwork | 22.2 Saloon Main | 20.1 Lamps bedroom | 20.4 WL6 bedroom | 20.3 FL2 Saloon | 20.5 Chandelier | COURTAINS OPEN | COURTAINS CLOSE | CHIME | SPARE | Sheers Open | Sheers Close | MASTER (Rented & Occ) | HEATING MAT | SALOON COURTAINS OPEN | SALOON COURTAINS CLOSE | SPARE | SPARE | Sheers Open | Sheers Close | SPARE | SPARE | FAN LOW | FAN MED | FAN HIGH | SPARE | COOL | HEAT | SPARE | SPARE | FAN LOW | FAN MED | FAN HIGH | SPARE | COOL | HEAT | SPARE | SPARE
BUS | [5 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 2 | 1 | 1 | 2 | 2
Location | [5 empty] | BATH | BATH | BED | BED | BED | BED | SALOON | SALOON | BATH | BED | SALOON | SALOON | BED | BED | SALOON | SALOON | BED | BATH | SALOON | SALOON
Circuit Control Device | [5 empty] | X10-1 | X10-1 | X10-2 | X10-2 | X10-3 | X10-3 | X10-4 | X10-4 | X10-5 | X10-5 | X10-6 | X10-6 | X10-7 | X10-7 | X10-8 | X10-8 | D254_1/1 | D254_1/2 | D254_2/1 | D454_2/2 | X05R_1_K1 | X05R_1_K2 | X05R_1_K3 | X05R_1_K4 | X05R_1_K5 | X05R_1_K6 | X05R_1_K7 | X05R_1_K8 | X05R_2_K1 | X05R_2_K2 | X05R_2_K3 | X05R_2_K4 | X05R_2_K5 | X05R_2_K6 | X05R_2_K7 | X05R_2_K8 | X05R_3_K1 | X05R_3_K2 | X05R_3_K3 | X05R_3_K4 | X05R_3_K5 | X05R_3_K6 | X05R_3_K7 | X05R_3_K8 | X05R_4_K1 | X05R_4_K2 | X05R_4_K3 | X05R_4_K4 | X05R_4_K5 | X05R_4_K6 | X05R_4_K7 | X05R_4_K8
IO Map | [5 empty] | 0 | 0 | 101 | 101 | 102 | 102 | 96 | 96 | 94 | 94 | 95 | 95 | 93 | 93 | 97 | 97 | 0 | 0 | 82 | 82 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
Device ID | [5 empty] | 100 | 100 | 101 | 101 | 102 | 102 | 96 | 96 | 104 | 104 | 105 | 105 | 103 | 103 | 97 | 97 | 106 | 106 | 82 | 82 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 109 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
Logical Circuit 0 | [5 empty] | 101 | 102 | 103 | 104 | 106 | 105 | 130 |  | 109 | 111 | 110 | 117 | 107 | 113 | 118 | 119 | 112 | 115 | 132 | 116 | 1 | 1 |  |  | 2 | 2 |  | 114 | 2 | 2 |  |  | 1 | 1
Logical Circuit 1 | [7 empty] | 120 | 120 | 120 | 120 |  |  |  | 120 |  |  | 120 |  |  |  | 120 | 120
Logical Circuit 2 | [7 empty] | 121 | 121 | 121 | 121 |  |  |  | 121 |  |  | 121 |  |  |  | 121 | 121
Logical Circuit 3 | [7 empty] | 122 | [5 empty] | 122
Fixture Drawing Designation
Lamp Type | [5 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Wattage | [5 empty] | 35 | 88 | 110 | 44 | 44 | 44 | 22 | 22 | 55 | 22 | 22 | 22 | 22 | 22 | 44 | 44 | 100 | 60 | 100 | 100
Dim Type | [5 empty] | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | None | None | None | None
WELCOME FIRST + RESTORE |  |  |  | Set Scene 0 |  | 30 | 20 | 100 | 100 | 60 | 60 | 100 |  | 100 | 80 | 90 | 80 | 100 | 80 | 60 | 60 | 80 | 80 | 80 | 80 | on | [5 empty] | FIDELIO |  | on
Switch # | Switch Location | AE Spec | Button | Text | AE Sw Function
CONNECT |  | SW:1 | 1
OneButton |  | Addr: 31 | 2 | Toggle Scene 13 | MASTER ON/OFF | [6 empty] | 100/0 |  |  |  | 100/0 | 100/0 |  |  | 100/0 | 100/0 |  |  | 100/0 | 100/0
3
Bethroom |  | IOMap: 31 | 4
5
6
ENTRANCE_B |  | SW: 5 | 1 | Set Scene 11 | DAY | [6 empty] | 100 |  |  |  | 90 | 80 |  |  | 60 | 60 |  |  | 80 | 80
|  | Addr: 25 | 2 | Set Scene 12 | EVENING | [6 empty] | 100 |  |  |  | 15 | 30 |  |  | 10 | 10 |  |  | 30 | 30
|  |  | 3 | X05R_1-K5 | OPEN COURTAINS | [24 empty] | ON
|  |  | 4 | X05R_1-K1 | MASTER ON/OFF | [6 empty] | 100/0 |  |  |  | 100/0 | 100/0 |  |  | 100/0 | 100/0 |  |  | 100/0 | 100/0 | [8 empty] | ON
Entrance |  | IOMap: 0 | 5 | Toggle Scene 13 | DND
|  |  | 6 | DND | CLOSE COURTAINS
|  |  | 7 | X05R_1-K6 | CLOSE SHEER | [25 empty] | ON
|  |  | 8 | X05R_1-K2 | CLOSE COURTAINS | [29 empty] | ON
CONNECT |  | SW:1 | 1
OneButton |  | Addr: 51 | 2 | Toggle Scene 13 | MASTER ON/OFF | [6 empty] | 100/0 |  |  |  | 100/0 | 100/0 |  |  | 100/0 | 100/0 |  |  | 100/0 | 100/0
3
Bethroom |  | IOMap: 51 | 4
5
6
CONNECT |  | SW: 1 | 1
OneButton |  | Addr: 41 | 2 | Toggle Scene 10 | MASTER ON/OFF |  |  | 100/0 | 100/0 | 100/0 | 100/0 |  |  |  | 100/0 |  |  | 100/0 |  |  |  | 100/0 | 100/0
3
Bethroom |  | IOMap: 41 | 4
5
6
BATHROOM |  | SW: 1 | 1 | Set Scene 5 | TOILET DAY | 50 | 50 | [6 empty] | 60 |  |  |  |  | 55 | [13 empty] | ON
ThreeButton |  | Addr: 19 | 2
|  |  | 3 | Set Scene 6 | TOILET NIGHT | 10 | 10 | [6 empty] | 30 |  |  |  |  | 25 | [13 empty] | ON
Bethroom |  | IOMap: 0 | 4
5
|  |  | 6 | Toggle Scene 7 | MASTER ON/OFF TOILET | 100/0 | 100/0 | [6 empty] | 100/0 |  |  |  |  | 100/0 | [13 empty] | ON/OFF
BEDSIDE A |  | SW: 6 | 1 | Set Log 120 | DAY |  |  | 80 | 80 | 80 | 80 |  |  |  | 80 |  |  | 80 |  |  |  | 80 | 80
FiveButton |  | Addr: 17 | 2 | Set Log 121 | EVENING |  |  | 40 | 40 | 40 | 40 |  |  |  | 40 |  |  | 40 |  |  |  | 40 | 40
|  |  | 3 | Set Scene 9 | NIGHT | 0 | 0 | 80 | 0 | 0 | 0 |  |  | 80 | 0 |  |  | 0 | 0 |  |  | 0 | 0
BedsideR |  | IOMap: 1 | 4 | Toggle Scene 3 | MASTER ON/OFF | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 |  |  | 100/0 | 100/0 |  |  | 100 | 100/0 |  |  | 100/0 | 100/0
|  |  | 5 | DND | DND
FourButton |  |  | 6 | AC AUTO/OFF | AC AUTO/OFF
|  |  | 1 | X05R_1-K1 | OPEN COURTAINS | [20 empty] | ON
BedsideR |  |  | 2 | X05R_1-K2 | CLOSE COURTAINS | [21 empty] | ON
RIGHT |  |  | 3
BedsideR |  |  | 4 | DIM UP | SLIDER
|  |  | 5 | DIM DOWN
|  |  | 6 | Log circ 120, 121,122
BEDSIDE B |  | SW: 7 | 1 | DIM UP | SLIDER
FourButton |  | Addr: 18 | 2 | DIM DOWN
|  |  | 3 | Log circ 120, 121,122
BedsideL |  | IOMap: 1 | 4 | X05R_1-K2 | CLOSE COURTAINS | [21 empty] | ON
|  |  | 5 | X05R_1-K1 | OPEN COURTAINS | [20 empty] | ON
LEFT |  |  | 6
|  |  | 1 | Set Log 120 | DAY |  |  | 80 | 80 | 80 | 80 |  |  |  | 80 |  |  | 80 |  |  |  | 80 | 80
FiveButton |  |  | 2 | Set Log 121 | EVENING |  |  | 40 | 40 | 40 | 40 |  |  |  | 40 |  |  | 40 |  |  |  | 40 | 40
|  |  | 3 | Set Scene 9 | NIGHT | 0 | 0 | 80 | 0 | 0 | 0 |  |  | 80 | 0 |  |  | 0 | 0 |  |  | 0 | 0
|  |  | 4 | Toggle Scene 3 | MASTER ON/OFF | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 |  |  | 100/0 | 100/0 |  |  | 100 | 100/0 |  |  | 100/0 | 100/0
|  |  | 5 |  | DND
LEFT |  |  | 6 |  | AC AUTO/OFF