## Sign-Off Sheet
Hotel Europejski
,
Switch Function Table Approval
|  | Switch Table: | Design:
|  | Switch Table Date: | Design Date: | 2016-03-09 10:03
Approved:
Date:
APPROVAL OF DESIGN IS REQUIRED PRIOR TO ANY PROGRAMMING OF INNCOM DEVICES. NO REPLY REGARDING APPROVAL DOES NOT CONSTITUTE ACCEPTANCE OR APPROVAL OF DESIGN.
Revision History
Date | Revision | Comments

## MOCKUP
INNCOM Switch Function Table
| Designer: | Maciej Jakubiak | [6 empty] | Design: |  | Design Date: | 2017-07-19
| Hotel Europejski |  |  |  |  | Controlled Zones/ Drapes | Controlled Zones/ Drapes |  | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes |  | Controlled Zones/ Drapes | Controlled Zones/ Drapes
| TypD-Flr1 |  |  |  |  | 6.1 SPARE | 6.2 Toilet Main | 7.1 Bed Screen | 7.1 Cabinet Bed (FOLOWING CIRCUIT FOR MASTER ON/OFF BEDROOM) | 8.1 Main Corridor | 8.2 Foyer | 9.1 Cabinet 1 | 20.2 Lamps Bathroom | 10.1 LED Toilet (FOLOWING CIRCUIT FOR MASTER ON/OFF BATHROOM) | 10.2 Minibar | 11.1 Main Bed LED | 20.1 Lamps bedroom |  | COURTAINS OPEN | COURTAINS CLOSE | CHIME | SPARE | SHEER OPEN | SHEER CLOSE | MASTER (Rented & Occ) | HEATING MAT | FAN LOW | FAN MED | FAN HIGH | SPARE | COOL | HEAT | SPARE | SPARE
Circuit Control Device | [5 empty] | X10-1 | X10-1 | X10-2 | X10-2 | X10-3 | X10-3 | X10-4 | X10-4 | X10-5 | X10-5 | X10-6 | D254_1/1 | D254_2/2 | X05R_1_K1 | X05R_1_K2 | X05R_1_K3 | X05R_1_K4 | X05R_1_K5 | X05R_1_K6 | X05R_1_K7 | X05R_1_K8 | X05R_2_K1 | X05R_2_K2 | X05R_2_K3 | X05R_2_K4 | X05R_2_K5 | X05R_2_K6 | X05R_2_K7 | X05R_2_K8
IO Map | [5 empty] | 0 | 0 | 201 | 201 | 102 | 102 | 103 | 103 | 104 | 104 | 105 | 80 | 80 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
Device ID | [5 empty] | 100 | 100 | 101 | 101 | 102 | 102 | 103 | 103 | 104 | 104 | 105 | 80 | 80 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
Logical Circuit 0 | [5 empty] | 101 | 102 | 104 | 103 | 105 | 106 | 107 | 113 | 109 | 110 | 111 | 112 |  | 1 | 1 |  |  | 2 | 2 |  | 114
Logical Circuit 1 | [7 empty] | 120 | 120 | 120 | 120 | 120 |  |  | 120 | 120 | 120
Logical Circuit 2 | [7 empty] | 121 | 121 | 121 | 121 | 121 |  |  | 121 | 121 | 121
Logical Circuit 3 | [8 empty] | 122 |  |  |  |  | 122
Fixture Drawing Designation
Lamp Type | [5 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Wattage | [5 empty] | 35 | 88 | 44 | 110 | 44 | 44 | 22 | 22 | 55 | 22 | 22 | 100 | 60
Dim Type | [5 empty] | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | None | None
WELCOME FIRST + RESTORE |  |  |  | Set Scene 0 |  |  | 20 | 100 | 100 | 60 | 60 | 100 | 80 | 100 | 90 | 80 | 80 |  | on |  |  |  | on |  | FIDELIO
Switch # | Switch Location | AE Spec | Button | Text | AE Sw Function
ENTRANCE_A |  | SW: 4 | 1 | Set Scene 1 | DAY |  |  | 100 | 100 | 60 | 60 | 100 |  |  | 90 | 80 | 80
FourButton |  | Addr: 16 | 2
|  |  | 3 | Set Scene 2 | EVENING |  |  | 60 | 40 | 10 | 10 | 100 |  |  | 15 | 30 | 30
Entrance |  | IOMap: 0 | 4 | Toggle Scene 3 | MASTER ON/OFF |  | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0
5
|  |  | 6 |  | DND
BEDSIDE A |  | SW: 2 | 1 | Set Scene 1 | DAY |  |  | 100 | 100 | 60 | 60 | 100 |  |  | 90 | 80 | 80
FiveButton |  | Addr: 17 | 2 | Set Scene 2 | EVENING |  |  | 60 | 40 | 10 | 10 | 100 |  |  | 15 | 30 | 30
LEFT |  | IOMap: 0 | 3 | X05R_1-K6 | CLOSE SHEER | [18 empty] | ON
BedsideR |  |  | 4 | X05R_1-K2 | CLOSE COURTAINS | [14 empty] | ON
|  |  | 5 | Toggle Scene 3 | MASTER ON/OFF |  | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0
|  |  | 6 | Set Scene 9 | NIGHT |  | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0
|  |  | 7 | X05R_1-K5 | OPEN SHEER | [17 empty] | ON
|  |  | 8 | X05R1-K1 | OPEN COURTAINS | [13 empty] | ON
|  |  | 1 | DND | DND
FourButton |  |  | 2 | AC AUTO/OFF | AC AUTO/OFF
RIGHT |  |  | 3
BedsideR |  |  | 4
|  |  | 5 | DIM UP | SLIDER
|  |  | 6 | DIM DOWN
|  |  | 7 | Log circ 120, 121,122
8
BEDSIDE B |  | SW: 3 | 1 | DIM UP | SLIDER
FourButton |  | Addr: 18 | 2 | DIM DOWN
|  | IOMap: 0 | 3 | Log circ 120, 121,122
4
|  |  | 5 |  | DND
LEFT |  |  | 6 |  | AC AUTO/OFF
BedsideL |  |  | 7
8
|  |  | 1 | Toggle Scene 3 | MASTER ON/OFF |  | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 | 100/0
FiveButton |  |  | 2 | Set Log 122 | NIGHT |  | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0
|  |  | 3 | X05R_1-K5 | OPEN SHEER | [17 empty] | ON
|  |  | 4 | X05R_1-K1 | OPEN COURTAINS | [13 empty] | ON
|  |  | 5 | Set Log 120 | DAY |  |  | 100 | 100 | 60 | 60 | 100 |  |  | 90 | 80 | 80
|  |  | 6 | Set Log 121 | EVENING |  |  | 60 | 40 | 10 | 10 | 100 |  |  | 15 | 30 | 30
RIGHT |  |  | 7 | X05R_1-K6 | CLOSE SHEER | [18 empty] | ON
BedsideL |  |  | 8 | X05R_1-K2 | CLOSE COURTAINS | [14 empty] | ON
BATHROOM |  | SW: 1 | 1 | Set Scene 5 | TOILET DAY |  | 50 | [5 empty] | 60 | 60 | [11 empty] | ON
ThreeButton |  | Addr: 10 | 2
|  |  | 3 | Set Scene 6 | TOILET NIGHT |  | 10 | [5 empty] | 30 | 30 | [11 empty] | ON
Bethroom |  | IOMap: 10 | 4
5
|  |  | 6 | Toggle Scene 7 | MASTER ON/OFF TOILET |  | 100/0 | [5 empty] | 100/0 | 100/0 | [11 empty] | ON/OFF
CONNECT |  | SW: 1 | 1
OneButton |  | Addr: 41 | 2 | Toggle Scene 10 | MASTER ON/OFF |  |  | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 |  |  | 100/0 | 100/0 | 100/0
3
Bethroom |  | IOMap: 41 | 4
5
6