## Sign-Off Sheet
Hotel Europejski
,
Switch Function Table Approval
|  | Switch Table: | Design:
|  | Switch Table Date: | Design Date: | 2016-03-09 10:03
Approved:
Date:
APPROVAL OF DESIGN IS REQUIRED PRIOR TO ANY PROGRAMMING OF INNCOM DEVICES. NO REPLY REGARDING APPROVAL DOES NOT CONSTITUTE ACCEPTANCE OR APPROVAL OF DESIGN.
Revision History
Date | Revision | Comments

## MOCKUP
INNCOM Switch Function Table
| Designer: | Maciej Jakubiak | [5 empty] | Design: |  |  | Design Date: | 2017-07-19
| Hotel Europejski |  |  |  |  | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes | Controlled Zones/ Drapes |  | Controlled Zones/ Drapes
| Type-H-Floor3 |  |  |  |  | 6.1 Toilet Accent | 6.2 Toilet Main | 7.1 Cabinet Bed (FOLOWING CIRCUIT FOR MASTER ON/OFF BEDROOM) | 7.2 Bed Screen | 8.1 Bedroom Artwork | SPARE | 9.1 Cabinet 1 | 8.2 WL3 Mirror Toilet | 10.1 LED Toilet | 10.2 Spare | 11.1 Main Bed LED | 20.3 Bedroom WL6 | SPARE | SPARE | CHIME | SPARE | SHEER OPEN | SHEER CLOSE | MASTER (Rented & Occ) | HEATING MAT | FAN LOW | FAN MED | FAN HIGH | SPARE | COOL | HEAT | SPARE | SPARE
Circuit Control Device | [5 empty] | X10-1 | X10-1 | X10-2 | X10-2 | X10-3 | X10-3 | X10-4 | X10-4 | X10-5 | X10-5 | X10-6 | D254_1/1 | X05R_1_K1 | X05R_1_K2 | X05R_1_K3 | X05R_1_K4 | X05R_1_K5 | X05R_1_K6 | X05R_1_K7 | X05R_1_K8 | X05R_2_K1 | X05R_2_K2 | X05R_2_K3 | X05R_2_K4 | X05R_2_K5 | X05R_2_K6 | X05R_2_K7 | X05R_2_K8
IO Map | [5 empty] | 0 | 0 | 101 | 101 | 102 | 102 | 103 | 103 | 104 | 104 | 105 | 0 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
Device ID | [5 empty] | 100 | 100 | 101 | 101 | 102 | 102 | 103 | 103 | 104 | 104 | 105 | 106 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
Logical Circuit 0 | [5 empty] | 101 | 102 | 103 | 104 | 105 | 106 | 107 | 113 | 109 | 110 | 111 | 112 | 1 | 1 |  |  | 1 | 1 |  | 114
Logical Circuit 1 | [7 empty] | 120 | 120 | 120 | 120 | 120 |  |  | 120 | 120 | 120
Logical Circuit 2 | [7 empty] | 121 | 121 | 121 | 121 | 121 |  |  | 121 | 121 | 121
Logical Circuit 3 | [7 empty] | 122 | [5 empty] | 122
Fixture Drawing Designation
Lamp Type | [5 empty] | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Wattage | [5 empty] | 35 | 88 | 110 | 44 | 44 | 44 | 22 | 22 | 55 | 22 | 22 | 100
Dim Type | [5 empty] | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | ZeroToTenVolts | None
WELCOME FIRST + RESTORE |  |  |  | Set Scene 0 |  | 30 | 20 | 100 | 100 | 60 |  | 100 | 80 | 100 |  | 80 | 80 |  |  |  |  | on |  | FIDELIO
Switch # | Switch Location | AE Spec | Button | Text | AE Sw Function
ENTRANCE_A |  | SW: 4 | 1 | Set Scene 1 | DAY |  |  | 100 | 100 | 60 |  | 100 |  |  |  | 80 | 80
FourButton |  | Addr: 16 | 2
|  |  | 3 | Set Scene 2 | EVENING |  |  | 40 | 60 | 10 |  | 100 |  |  |  | 30 | 30
Entrance |  | IOMap: 0 | 4 | Toggle Scene 3 | MASTER ON/OFF | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 |  | 100 | 100/0 | 100/0 |  | 100/0 | 100/0
5
|  |  | 6 |  | DND
BEDSIDE A |  | SW: 6 | 1 | Set Scene 1 | DAY |  |  | 100 | 100 | 60 |  | 100 |  |  |  | 80 | 80
FiveButton |  | Addr: 17 | 2 | Set Scene 2 | EVENING |  |  | 40 | 60 | 10 |  | 100 |  |  |  | 30 | 30
|  |  | 3 | Set Scene 9 | NIGHT | 0 | 0 | 80 | 0 | 0 |  | 0 | 0 | 80 |  | 0 | 0
LEFT |  | IOMap: 0 | 4 | Toggle Scene 3 | MASTER ON/OFF | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 |  | 100 | 100/0 | 100/0 |  | 100/0 | 100/0
BedsideR |  |  | 5 | DND | DND
|  |  | 6 | AC AUTO/OFF | AC AUTO/OFF
|  |  | 1 | X05R_1-K5 | OPEN SHEER | [16 empty] | ON
|  |  | 2 | X05R_1-K6 | CLOSE SHEER | [17 empty] | ON
3
FourButton |  |  | 4 | DIM UP | SLIDER
RIGHT |  |  | 5 | DIM DOWN
BedsideR |  |  | 6 | Log circ 120, 121,122
BEDSIDE B |  | SW: 7 | 1 | DIM UP | SLIDER
FourButton |  | Addr: 18 | 2 | DIM DOWN
LEFT |  |  | 3 | Log circ 120, 121,122
BedsideL |  | IOMap: 0 | 4 | X05R_1-K5 | OPEN SHEER | [16 empty] | ON
|  |  | 5 | X05R_1-K6 | CLOSE SHEER | [17 empty] | ON
6
LEFT |  |  | 1 | Toggle Scene 3 | MASTER ON/OFF | 100/0 | 100/0 | 100/0 | 100/0 | 100/0 |  | 100 | 100/0 | 100/0 |  | 100/0 | 100/0
BedsideR |  |  | 2 | DND | DND
|  |  | 3 | AC AUTO/OFF | AC AUTO/OFF
FiveButton |  |  | 4 | Set Scene 1 | DAY |  |  | 100 | 100 | 60 |  | 100 |  |  |  | 80 | 80
BedsideL |  |  | 5 | Set Scene 2 | EVENING |  |  | 40 | 60 | 10 |  | 100 |  |  |  | 30 | 30
|  |  | 6 | Set Scene 9 | NIGHT | 0 | 0 | 80 | 0 | 0 |  | 0 | 0 | 80 |  | 0 | 0
BATHROOM |  | SW: 1 | 1 | Set Scene 5 | TOILET DAY | 50 | 50 | [5 empty] | 60 | 60 | [10 empty] | ON
ThreeButton |  | Addr: 19 | 2
|  |  | 3 | Set Scene 6 | TOILET NIGHT | 10 | 10 | [5 empty] | 30 | 30 | [10 empty] | ON
Bethroom |  | IOMap: 0 | 4
5
|  |  | 6 | Toggle Scene 7 | MASTER ON/OFF TOILET | 100/0 | 100/0 | [5 empty] | 100/0 | 100/0 | [10 empty] | ON/OFF